## Sheet1
Steam |  | Enlhalpy kJ/kg |  | Entropy kJ/(kg.K) |  | Density kg/m3 |  | Mixture
Pressure kPa.a | Temperature ºC | Liquid | Vapour | Liquid | Vapour | Liquid | Vapour | Enthalpy kJ/kg | Entropy kJ/(kg.K) | Density kg/m3 | Quality % | Speed m/s | Mass flux kg/s/m2 |  | k
2000 | 212.36 | 908.59 | 2797.2 | 2.4469 | 6.3366 | 849.907 | 10.047 | 2797.2 | 6.3366 | 10.047 | 100% | 0 | 0 | Initial Condition | 1.1306
1900 | 209.79 | 896.81 | 2796.1 | 2.4228 | 6.3554 | 853.097 | 9.556 | 2787.0203 | 6.3366 | 9.6014 | 99.52% | 142.6861 | 1369.9839 |  | 1.1296
1800 | 207.1 | 884.57 | 2794.8 | 2.3976 | 6.3751 | 856.311 | 9.065 | 2776.31 | 6.3366 | 9.1527 | 99.03% | 204.4014 | 1870.8156 |  | 1.1308
1700 | 204.3 | 871.84 | 2793.4 | 2.3713 | 6.3957 | 859.623 | 8.575 | 2765.1811 | 6.3366 | 8.7015 | 98.53% | 253.057 | 2201.9779 |  | 1.1307
1600 | 201.36 | 858.56 | 2791.7 | 2.3436 | 6.4175 | 863.111 | 8.085 | 2753.3115 | 6.3366 | 8.2472 | 98.01% | 296.2719 | 2443.4259 |  | 1.1331
1500 | 198.28 | 844.66 | 2789.9 | 2.3145 | 6.4406 | 866.707 | 7.596 | 2740.8694 | 6.3366 | 7.7906 | 97.48% | 335.6503 | 2614.9322 |  | 1.1305
1400 | 195.03 | 830.07 | 2787.8 | 2.2837 | 6.4651 | 870.398 | 7.106 | 2727.6363 | 6.3366 | 7.3294 | 96.93% | 372.9977 | 2733.8509 |  | 1.1336
1300 | 191.6 | 814.7 | 2785.4 | 2.251 | 6.4913 | 874.279 | 6.617 | 2713.5024 | 6.3366 | 6.8656 | 96.35% | 409.1395 | 2808.9814 |  | 1.1319
1200 | 187.95 | 798.43 | 2782.7 | 2.2161 | 6.5194 | 878.349 | 6.127 | 2698.4101 | 6.3366 | 6.3968 | 95.75% | 444.4994 | 2843.3897 |  | 1.1356
1156 | 186.27 | 790.95 | 2781.4 | 2.1999 | 6.5324 | 880.1267 | 5.9123 | 2691.445 | 6.3366 | 6.1902 | 95.48% | 459.9022 | 2846.8752 | Sonic Condition – Maximum Flux
1100 | 184.06 | 781.12 | 2779.7 | 2.1786 | 6.5497 | 882.535 | 5.638 | 2682.2652 | 6.3366 | 5.925 | 95.12% | 479.4473 | 2840.7302 |  | 1.133
1000 | 179.87 | 762.61 | 2776.2 | 2.1382 | 6.5828 | 887.075 | 5.147 | 2664.6611 | 6.3366 | 5.447 | 94.46% | 514.8571 | 2804.4132 |  | 1.1332
900 | 175.35 | 742.64 | 2772.1 | 2.0941 | 6.6192 | 891.822 | 4.655 | 2645.3569 | 6.3366 | 4.9634 | 93.75% | 551.0774 | 2735.1908 |  | 1.1341
800 | 170.4 | 720.94 | 2767.5 | 2.0457 | 6.6596 | 896.861 | 4.162 | 2624.2288 | 6.3366 | 4.4737 | 93% | 588.1686 | 2631.3102 |  | 1.1339
700 | 164.95 | 697.06 | 2762 | 1.9918 | 6.7052 | 902.364 | 3.667 | 2600.5164 | 6.3366 | 3.9767 | 92.18% | 627.19 | 2494.1629 |  | 1.135
600 | 158.83 | 670.42 | 2755.5 | 1.9308 | 6.7575 | 908.43 | 3.17 | 2573.6759 | 6.3366 | 3.4717 | 91.28% | 668.6166 | 2321.2246 |  | 1.1334
500 | 151.83 | 640.12 | 2747.5 | 1.8604 | 6.8192 | 915.08 | 2.669 | 2542.4057 | 6.3366 | 2.9558 | 90.27% | 713.8547 | 2110.0317
Sizing the conventional way: |  | (eg DIN or SWISS Standards)
k= |  | 1.1319 |  | log(2000/1156)/log(10.047/6.190) |  |  |  | This calculates the k value that matches Pv^k=constant from 2000 kPa to 1200 kPa
|  | 1.13 |  | Swiss Standard SVDB Band 2 |  |  |  | The Swiss standard specifies k= 1.13 for saturated steam at 2000 kPa.a
Note the “k” column on the right showing that 1.13 is indeed a fair assumption in this instance.
Mass Flux | 2844.566 | kg/s/m2 | [5 empty] | (before applying C or 0.9Kd)
Pcr | 1156.9079 | kPa
Speed of sound | 459.5801 | m/s