Determination of the minimum lengths of 
Syphons & other cooling extensions for field Instruments
(by J.J. Jacq)

- Introduction

It is common practice, when fitting a gauge or transmitter to a hot process stream, to thermally isolate the sensor from the process by a piece of pipe or tube to ensure that the temperature at the sensor is not excessive. In the case of steam or hot condensing vapours, this tube is fitted with a syphon or pig-tail to avoid the escape of condensate from the tube. In which case only the flooded section is effective.
The problem facing the instrument engineer is to choose the length of this pipe correctly. Too short a length will lead to excessive temperature at the instrument, too long a length will lead to an installation prone to mechanical damage (the syphons being for the most part unsupported and , when mounted horizontally, acting as excellent ladder rungs). The usual approach is to pick a length and hope for the best. 
The following article proposes a method of calculation which will remove the guesswork out of selecting the length (and may also help you keep the dreaded QA auditors at bay).

Analysis of a cooling tube of uniform cross section

Do 	= Cooling tube external diameter
Di 	= Cooling tube internal diameter 
b 	= DiD0
To 	= Process fluid temperature
Ta 	= Ambient temperature
T(x) 	= Temperature at x
k 	= Thermal conductivity of the metal
h 	= Heat transfer coefficient of the tube to the air
L 	= length of the tube
x 	= Distance from process to any point along the tube
						Q(x)	= Heat flux at x along the tube

		Figure 2.1

If we analyse an element of tube of length dx (refer figure 2.2), the heat balance equation can be described as :
	Heat entering at x  - Heat leaving at (x+dx) = Lateral heat losses over dx







 
Figure 2.2
	






The heat loss due to convection is given by the following formula:
		−dQ=p⋅D0⋅hTx−Ta⋅dx				2.1

- The heat flow, Q(x), at x is proportional to the temperature gradient along the pipe at x:

		Qx=-p⋅D021−β24⋅k⋅dTxdx 				2.2
Taking the derivative relative to x we get:
		dQdx=-p⋅D02⋅1−β24⋅k⋅d2Txdx2				2.3
By combining 2.1 & 2.3 we get the general differential equation:
	hTx−Ta=D01−β24⋅k⋅d2T(x)dx2				2.4
By integration we obtain the following general equation:
	Tx=Ta+A⋅e4h1−β2⋅D0⋅k.x+B⋅e−4h1−β2⋅D0⋅k⋅x			2.5
	where A & B are constants.
The only assumption made has been that the heat transfer coefficient, h, remains constant along the length of the cooling tube, this is not quite true as it depends to some extent on the temperature T(x) which is itself variable. In practice , we assume calculate h for T= To and for T= TL , the desired temperature at the end of the tube , and use the average value for h. 
A & B are chosen to satisfy the boundary conditions. The conditions are:
		T0=ToTemperatureatx=0Q(L)=0Noheatflowatx=L

From these two conditions we determine A & B and the equation finally becomes:
	Tx=Ta+T0−Ta⋅cosh1−x⋅4h1−β2⋅D0⋅kcoshL⋅4h1−β2⋅D0⋅k	2.6
And the temperature which is of interest to us , TL , is given simply by:



		2.7	


or



  2.8

TL=Ta+T0−TacoshL⋅4h1−β2⋅D0⋅k

L=1−β2⋅D0⋅k4h⋅cosh−1T0−TaTL−Ta

- Determination of the heat transfer coefficients

For a horizontal tube, with natural convection only (worst case), we have:
		h=4.66LMTDD014						3.1
		with 	h in kJm2⋅°C⋅hour,
			LMTD = Log Mean Temperature Difference (°C)
			Do in metres

For a vertical tube, with natural convection, we have:
		h=5.2LMTDL14						3.2
		with the same units as previously and L in metres.

And the LMTD is calculated as follows:

		LMTD=T0−Ta−TL−TaLnT0−TaTL−Ta				3.3

- Thermal conductivity of various metals

	Carbon steel			k	=	190   	kJ/m.°C.hour
	316SS/304SS			k	=	52     	kJ/m.°C.hour
	Copper			k	=	1380 	kJ/m.°C.hour
	(0.8Cr/0.5Mo) steel		k	=	157   	kJ/m.°C.hour
	Cupronickel(70Cu/30Ni)	k	=	103   	kJ/m.°C.hour
	Monel				k	=	83 	kJ/m.°C.hour

- Examples

Process temperature 400°C, maximum allowable temperature at the gauge 60°C.
Ambient temperature 40°C.
The cooling pipe is made of 19mm (3/4”) carbon steel pipe
	Do	= 26.6 mm
	Di 	= 20.9 mm
	k	= 190 kJ/m.°C.hour

For a horizontal pipe the problem is easy as Do is known:
	LMTD	= 118°C			based on 3.3
	h		= 38 kJm2⋅°C⋅hour	based on 3.1
	L		=  0.404m	 = 404 mm	based on 2.8

- For a vertical pipe the problem is more complicated as L is not known. Let’s start by assuming L=400mm.
	L= 0.4 m gives 		h1 = 21.6 kJm2⋅°C⋅hour	based on 3.2
	L1= 0.536 m								based on 2.8
Using L1 =0.536 m we get 	h2 = 20.0 kJm2⋅°C⋅hour
	L2=0.557 mm

Using L2 = 0.557 m we get	h3 = 19.8 kJm2⋅°C⋅hour
	L3= 0.560 mm

At this stage, the iteration is sufficient, Lmin = 560mm.

Note that this applies only to the flooded section of tubing when dealing with condensing vapours.

- Other Considerations

The heat has been assumed to travel in the metal and by conduction only. The fluid within the tube will also transport heat by conduction and also by convection. Allowance for this can be made by multiplying the fluid area (pDi24) by the fluid conductivity and dividing by the metal conductivity, this will give you the additional equivalent metal area to add to the tube (thereby giving an equivalent tube internal diameter, smaller than the actual one, to account for the fluid conductivity). Alternatively, leave the tube dimensions as they are and calculate an equivalent metal conductivity to allow for the fluid conductivity :k=km+kL⋅Di2D02−Di2. For most liquids, this correction is small, for gases it is negligible.
The effect of convection is not so easy to predict. For a horizontal tube it can be neglected. For a vertical tube pointing upward the effect will be maximum, if it points downward the effect will not exist at all. My own approach is to allow for conductivity for liquids and ignore internal convection as the external natural convection assumption on the outside of the tube is often pessimistic (ie there is wind or air draft more often than not, and the ambient temperature chosen is often the highest possible one can dream of). To minimise convection, the internal diameter should be as small as possible

copyright © 1997 - JJ & DJ Jacq Pty Ltd